Technical & Root Cause

- What specifically triggered the 200H alarm on Inverters 19 and 20?

  - The 200H alarm is the alarm code sent by the Ground Fault Circuit Interrupter (GFCI) when triggered, this protection device only triggered when there is leaking of current from Hot/Live line going to the ground. Since both Inverters were protected with GFCI and located on the same Block Station with common ground, it is assumed that before/during the fire incident, one of the live/hot lines of the Inverter 19's AC side was shorted to the ground triggering the GFCI of each inverter to send signal to the electronic measurement board and converting it to 200H alarm code.

- Was the fire in Inverter 19 caused by a component failure (e.g., IGBT, capacitor, DC bus) or an external factor such as SCB wiring?

  - Upon thorough checking of the Inverter Engineer right after responding to the incident location, it was found out that the Main AC Breaker and the Bus bar of the Inverter 19 where it connected were the ones with most severe damaged, the busbar of Line 2 of the 3-Phase lines was totally melted indicating it was the main sources of the fire. It was verified by the Inverter Engineer that the entire DC side (from Panels going to SCBs' wirings) was not contributing to this incident, this incident only involves and occurred on the AC-side alone of the Inverter 19.

- Did Inverter 20 sustain any damage, or was its alarm purely a secondary effect?

  - Inverter 20 did not sustain any damage; it only detected current leakage from Inverter 19 where the fire happened. The alarm 200H it recorded was purely a secondary effect and for its self-protection.

- Were there any abnormal operating conditions (temperature, load, dust, humidity) prior to the incident?

  - All Inverters are all simultaneously and realtime monitored with our  Inverter Dashboard, before the incident occurs, Operations Engineer and the Inverter Engineer can confirm that there are no abnormal operating conditions occurring on Inverter 19, there have no recorded any alarms prior to the incident. The alarm logs can be monitored and downloaded in the dashboard.

- Are the protection settings (trip thresholds, relay coordination) aligned with design standards?

  - All protection configurations were the default set by Ingeteam here in our plant, there were no re-configuration made to this inverter prior to the incident.

Safety & Operations

- Were there any injuries or safety hazards to personnel during the fire response?

  - None.

- Did the incident affect grid stability or plant output beyond Blocks 10 and 11?

  - To be confirmed by the operations team.

- How effective was the fire suppression response — were extinguishers adequate, or should additional measures be installed?

  - Fire suppression response was immediate and very effective, the fire extinguisher was accessible and ready to use. One (1) fire extinguisher was already enough to handle such a fire.

Equipment & Maintenance

- What parts of Inverter 19 are confirmed damaged and require replacement?

  - According to the inspection and visual assessment of the Inverter Engineer after the fire suppression, all 4 Power Blocks installed were not caught on fire, assuming they are still operational. However, in the cabinet location (Cabinet 1) where the fire started, all components and devices there were burned, wires were melted and the entire cabinet is unsafe to be reoccupied with new parts replacement. Here are list of the damaged components:

    - Main AC Breaker and Bus bar (totally burnt and melted)

    - DC Isolator (burnt)

    - CMC (burnt)

    - Thermal breaker (burnt)

    - Timer delay relays (burnt)

    - DC Isolator cooling fan (burnt)

    - AC Cables and wirings (burnt)

    - Surge Protection devices (burnt)

    - Hinges of the Door (melted)

    - Component Mountings (melted)

    - Plastic covers and paints (burnt)

- Are there preventive maintenance records showing prior issues with Inverter 19 or 20?

  - Quarterly PMS of these inverters was conducted last July 22, 2026. There were no prior issues occurring on these inverters especially Inverter 19, it was operating normally.

- Was there any recent servicing or modification to SCBs, RMU 10, or the affected inverters?

  - This should be confirmed by the Maintenance Team.

Financial & Insurance

- What is the estimated cost of replacement for the damaged components?

- Does the incident fall under the scope of the plant’s insurance coverage (fire/equipment breakdown)?

- Are there any warranty claims applicable for the inverter or its components?

Reporting & Next Steps

- When will the comprehensive root cause report be available?

- What corrective actions are being considered to prevent recurrence?

  - We will include in the quarterly PMS the thermal scanning on the major parts of the inverter. Also, retightening of the connection points of the bus bars and the protection devices in all inverters which requires special tools like a torque wrench.

- Should NGCP or other regulatory bodies be formally notified of the incident?

  - Operations team to answer