## Investigation Checklist
Phase | Task | Description | Status | Notes
Phase 1: Immediate Action & Safety | Secure the Area | Ensure the area around the inverter is cordoned off. Verify no unauthorized personnel have access. | Pending
Phase 1: Immediate Action & Safety | Lockout/Tagout (LOTO) | Perform complete LOTO on both AC (Medium Voltage transformer/switchgear) and DC (array combiners/recombiners) sides. Verify zero voltage. | Pending
Phase 1: Immediate Action & Safety | Capacitor Discharge Check | Wait the manufacturer-specified time for DC link capacitors to discharge. Verify zero voltage across DC link before touching anything. | Pending
Phase 1: Immediate Action & Safety | Initial Photography | Take extensive high-resolution photos of the entire inverter, AC compartment, breaker, soot patterns, and surrounding environment BEFORE touching anything. | Pending
Phase 2: Data Gathering | ADSI Dashboard - Alarm Export | Go to the ADSI Dashboard Alarms page. Export recent alarms for this inverter. Look for preceding codes like 0x0020H or 0x7FFF (Fatal Error). | Pending
Phase 2: Data Gathering | ADSI Dashboard - Audit Export | Go to the ADSI Dashboard Audit page. Export audit logs to check if any manual START/STOP commands (or Bulk Control) were issued prior to the fire. | Pending
Phase 2: Data Gathering | ADSI Dashboard - Parameters Log | Check the Parameters (Energy) page for the 5-minute node-level PAC and PDC logs leading up to the failure. | Pending
Phase 2: Data Gathering | Protection Relay Data | Download event records and oscillography from the AC protection relay (if external at the MV station) or inverter internal grid monitor. | Pending
Phase 2: Data Gathering | Maintenance Records Review | Collect recent PM reports, especially IR (Infrared) thermography reports, torque checks, and previous breaker operations. | Pending
Phase 3: Visual Inspection | AC Breaker Compartment | Inspect the main AC breaker for the epicenter of the fire. Look for melted terminals, vaporized copper/aluminum, and direction of soot/arc flash propagation. | Pending
Phase 3: Visual Inspection | Busbar and Terminations | Check for signs of loose connections (fretting, discoloration prior to the arc). Note if the failure originated at the lug/cable termination or inside the breaker mechanism. | Pending
Phase 3: Visual Inspection | Environmental & Mechanical | Check for signs of water ingress, vermin, insect nests, dust accumulation, or blocked ventilation filters that could cause overheating. | Pending
Phase 4: Electrical Testing | Cable Insulation Resistance | Test AC cables between the inverter and the MV transformer for insulation breakdown. (Ensure disconnected from sensitive electronics). | Pending
Phase 4: Electrical Testing | Torque Verification | Check the torque of surviving connections in the AC compartment to identify systemic under-torquing or thermal cycling relaxation. | Pending
Phase 4: Electrical Testing | DC Side Health Check | Perform insulation resistance testing on the DC side to ensure a severe DC ground fault didn't contribute to the AC side failure. | Pending
Phase 5: Component Analysis | Reference ADSI Manuals | Click any alarm hex code in the ADSI Dashboard to open the Alarm Drilldown. Download the Level 1 (AAV2011IMC01) & Level 2 (AAV2011IFA01) workflows. | Pending
Phase 5: Component Analysis | Reference Schematic AQM0027 | Download the AQM0027 schematic from the dashboard. Check p.6 for AC supply / RVAC / FAC fuses to verify damage to adjacent circuitry. | Pending
Phase 5: Component Analysis | Breaker Extraction | Carefully remove the failed breaker. Preserve it for potential metallurgical/forensic analysis by the manufacturer (Ingeteam) or a third party. | Pending
Phase 5: Component Analysis | Contact Ingeteam Support | Open a severe incident ticket with Ingeteam Support. Provide them with the initial photos, serial number, ADSI alarm exports, and fault logs. | Pending
Phase 6: Root Cause Analysis | Evaluate Loose Connection | Determine if the fire started at the terminal (often due to thermal cycling, improper torque). Check history of high temps in recent IR scans. | Pending
Phase 6: Root Cause Analysis | Evaluate Breaker Failure | Determine if internal contacts failed to open under load or short circuit, or if the arc chute failed. | Pending
Phase 6: Root Cause Analysis | Evaluate External Fault | Investigate if there was a significant grid event (voltage spike, short circuit on the MV side) that the breaker attempted to clear and failed. | Pending
Phase 7: Remediation Plan | Clean and Vacuum | Thoroughly clean all soot and debris from the compartment using specialized non-conductive cleaners to prevent tracking faults. | Pending
Phase 7: Remediation Plan | Replace Components | Replace the breaker, damaged busbars, cables, and any heat-damaged control wiring nearby. | Pending
Phase 7: Remediation Plan | Pre-commissioning Tests | Perform full pre-commissioning checks (Megger, Ductor) on the new installation before re-energizing. Check ADSI Dashboard for successful telemetry. | Pending