# Fishbone (Ishikawa) Diagram Mapping

# Effect: Fire localized to Cabinet 1 (DCAC Supply Module)

## Hardware in Cabinet 1

AC Side: High resistance failure at the main AC breaker (QAC) or harmonic filter failure.

DC Side: Failure of the DC contactors (QDC1-4), DC fuses, or blocking diodes.

Auxiliary: Failure of QAUX or the 15V power supply circuitry.

## Procedures

Incomplete torque checks on AC/DC connections during PM

IR Thermal scan not conducted under sufficient load

## Environment

Vermin / Water Ingress via bottom cable entries

Dust or salt contamination accelerating oxidation

## Measurement

Protection relay failed to clear external fault

ADSI Dashboard precursor alarms not triggered or logged

## Materials

Degraded cable insulation

Missing spring washers or anti-oxidant compound

## Personnel

Early warning signs missed in visual inspection

Delayed operator response to SCADA telemetry alarms