# Compliant Preventive Maintenance Schedule (PMS)

Equipment: Ingecon Sun POWERMAX M DCAC Outdoor

Frequency: Quarterly / Annual

Compliance Baseline: Ingeteam Installation & Operation Manual + CAPA Directives

# 1. Operating Checks (Prior to Shutdown)

These steps MUST be performed while the inverter is actively exporting power to the grid (preferably >70% load).

| Task | Description / Spec | Done (Y/N) |
| --- | --- | --- |
| IR Thermal Scanning | [CAPA REQUIRED] Scan AC breaker (QAC), DC contactors (QDC), and all main busbars for hotspots. |  |
| Fan Operation | Verify all cooling fans are actively running without abnormal noise. |  |
| Alarm Log | Check the inverter display and ADSI Dashboard for active or historical alarms. |  |

# 2. Safety & LOTO (Shutdown)

| Task | Description / Spec | Done (Y/N) |
| --- | --- | --- |
| Safe Shutdown | Stop the inverter via display. Open AC and DC disconnects. |  |
| Capacitor Discharge | Wait at least 10 minutes for internal capacitors to discharge. |  |
| Voltage Check | Use a Class III 1000V multimeter to physically verify absence of AC and DC voltage. |  |

# 3. Cleaning & Environmental (Monthly/Quarterly)

| Task | Description / Spec | Done (Y/N) |
| --- | --- | --- |
| Filters & Grids | [Manual Sec 18.7] Remove and wash/vacuum the air inlet filters and rear deflectors. |  |
| Interior Cleaning | Vacuum any accumulated dust from the interior. Do not use compressed air. |  |
| Ingress Check | Inspect cable entries and bottom skirting for water, vermin, or salt ingress. Seal with neutral silicone if necessary. |  |

# 4. Mechanical & Electrical Connections (Torque Checks)

As per Ingeteam Manual Sec 18.5 and CAPA Requirements, use a calibrated torque wrench on all high-current joints.

| Task | Torque Specification | Done (Y/N) |
| --- | --- | --- |
| DC Input Connections | M12 Bolt -> 65 Nm |  |
| AC Output Connections | M12 Bolt -> 65 Nm |  |
| AC Breaker (QAC) & DC Switch Plates | M10 Bolt -> 39 Nm |  |
| General Ground Connections | M6 Bolt -> 8 Nm / M8 Bolt -> 19 Nm |  |

# 5. Component Checks

| Task | Description / Spec | Done (Y/N) |
| --- | --- | --- |
| Connection Plates | Visually inspect AC/DC busbars and plates for signs of heating, rust, or oxidation. |  |
| Cable Insulation | Check heavy power cables for discoloration or degradation. |  |
| Fuses & Varistors | Check AC/DC fuses. Verify varistors (RV1, RV2, RV3) show high impedance. |  |