# Root Cause Analysis (RCA)

Incident: Inverter 19 - AC Main Breaker Fire & L2 Busbar Melting

Date of Incident: [Insert Date]

RCA Lead: [Insert Name]

# 1. Problem Statement

The Line 2 (Phase B) copper/aluminum busbar connected to the 1600A ABB Thermal-Magnetic main AC breaker completely melted and severed, resulting in an arc flash, fire, and catastrophic failure of the AC compartment.

# 2. Fishbone (Ishikawa) Analysis

Evaluate each of the 6 categories to ensure no contributing factors are missed.

## A. Machine / Equipment (Hardware)

ABB Breaker: Did the L2 internal contacts fail, creating high internal resistance?

Busbar Integrity: Was there preexisting metallurgical stress, micro-cracks, or oxidation on the L2 busbar?

Vibration: Did 50/60Hz AC humming or cooling fans cause micro-vibrations that backed the bolt out over time?

## B. Method (Procedures)

Installation: Was the correct torque applied to the L2 bolt during initial commissioning?

Maintenance: Did the annual PM procedure explicitly require re-torquing the breaker terminals? If so, was it followed?

Thermal Scanning: Was Infrared (IR) thermography conducted under sufficient load (>70% capacity) to accurately detect a developing hotspot?

## C. Materials

Hardware: Were the correct washers used (e.g., Belleville/conical spring washers) to maintain tension during thermal expansion and contraction?

Anti-Oxidant: Was electrical joint compound (e.g., Noalox) applied to the connection if mating dissimilar metals or aluminum?

## D. Measurement (Data & Tools)

Torque Wrench Calibration: If the bolt was torqued during the last PM, was the torque wrench properly calibrated?

SCADA Telemetry: Did the ADSI Dashboard parameter logs show phase imbalances or voltage anomalies on L2 prior to the event?

## E. Environment

Thermal Cycling: The inverter operates outdoors. Did extreme day/night temperature swings accelerate the loosening of the joint?

Contamination: Was there dust, high humidity, or salt ingress that accelerated oxidation at the joint?

## F. People (Personnel)

Training: Was the technician performing the last PM aware of the specific torque requirements for a 1600A ABB breaker?

Fatigue/Oversight: Was the L2 connection simply missed during the last visual inspection?

# 3. The "5 Whys" Deep Dive

(Example based on the most likely hypothesis: Thermal Runaway)

1. Why did the breaker catch fire?
Because the L2 busbar experienced extreme thermal runaway and melted, triggering an arc flash.

2. Why did the L2 busbar experience thermal runaway?
Because the electrical contact resistance between the busbar and the breaker lug was abnormally high.

3. Why was the contact resistance high?
Because the bolt securing the busbar had loosened, allowing oxidation to form between the mating surfaces.

4. Why did the bolt loosen?
Because it was subjected to years of thermal expansion and contraction without a Belleville spring washer to maintain tension. (Or: Because it was not torqued to the manufacturer spec during the last PM).

5. Why was it not torqued to spec during the last PM?
Because the maintenance checklist did not explicitly require torque verification of the main AC breaker, relying only on visual inspection.

# 4. Corrective and Preventive Actions (CAPA)

| Action Item | Owner | Target Date | Status |
| --- | --- | --- | --- |
| Corrective: Replace damaged ABB breaker, busbars, and clean compartment. |  |  |  |
| Preventive 1: Update the PM checklist to mandate torque-wrench verification of all >400A connections. |  |  |  |
| Preventive 2: Ensure IR thermography is only conducted when the inverter is exporting >70% rated power. |  |  |  |
| Preventive 3: Standardize the use of Belleville (conical) washers on all high-current busbar connections. |  |  |  |