# Fishbone (Ishikawa) Diagram Mapping

# Effect: Unspecified Fire on Inverter 19

## Environment

Vermin / Water Ingress bridging live components

Clogged filters causing internal overtemperature

## Procedures

Incomplete torque checks on AC/DC connections during PM

IR Thermal scan not conducted under sufficient load

## Hardware

DC Side: Combiner fuse / switch failure

AC Side: Breaker / Harmonic filter failure

Power Stack: IGBT / DC-Link capacitor failure

## Measurement

Protection relay failed to clear external fault

ADSI Dashboard precursor alarms not triggered or logged

## Materials

Degraded cable insulation

Missing spring washers or anti-oxidant compound

## Personnel

Early warning signs missed in visual inspection

Delayed operator response to SCADA telemetry alarms