# Visual Fishbone (Editable Table Format)

| ENVIRONMENT • Vermin / Water ingress via bottom cables • Dust or salt contamination accelerating oxidation | PROCEDURES • Incomplete torque checks on AC/DC connections during PM • IR Thermal scan not conducted under sufficient load | HARDWARE (CABINET 1) • DC Side: QDC contactors / DC fuses • AC Side: QAC Breaker / Harmonic filter • Auxiliary: QAUX / control wiring | EFFECT: FIRE LOCALIZED TO CABINET 1 (DCAC SUPPLY MODULE) |
| --- | --- | --- | --- |
| =========================================================> | =========================================================> | =========================================================> |  |
| MEASUREMENT • Protection relay failed to clear external fault • ADSI Dashboard precursor alarms not triggered or logged | MATERIALS • Degraded cable insulation • Missing spring washers or anti-oxidant compound | PERSONNEL • Early warning signs missed in visual inspection • Delayed operator response to SCADA telemetry alarms |  |